## GUIDE
NOTE 1: | Trước khi thực hiện mô phỏng ổn định động, cần thực hiện cài đặt thông số trong file tính toán xác lập ở Tab "Machine" như sau:
LOẠI NGUỒN NLTT KHẢO SÁT
|  |  | Solar power | Wind power - Type 4 | Wind power - Type 3
|  | Xsource | 9999 | 9999 | 0.8
|  | Subtransient X | 9999 | 9999 | 0.8
|  | Transient X | 9999 | 9999 | 0.8
|  | Synchronous X | 9999 | 9999 | 0.8
|  | X-Negative | 9999 | 9999 | 0.8
|  | X-Zero | 9999 | 9999 | 0.8
|  | Machine Control Mode | Renewable +,- Q limit based on WPF | Renewable +,- Q limit based on WPF | Renewable +,- Q limit based on WPF
- Mô hình Solar và Wind Type 4 sẽ sử dụng cùng mô hình mô phỏng ổn định động nên cài đặt thông số giống nhau.
- Wind-Type 3: Doubly-fed asynchronous generators with rotor-side converter
- Wind-Type 4: Full-power converter interface
NOTE 2: | Hướng dẫn nhập thông số các mô hình ổn định động ở các sheet sau:
|  | Sheet | Mô hình
|  | SOLAR&WIND-TYPE4 | Solar power & Wind - Type 4 cho khảo sát biến động CS theo thời tiết và ngắn mạch
|  | WIND-TYPE3 CHO KB BDCS | Wind - Type 3 cho khảo sát biến động CS theo thời tiết
|  | WIND-TYPE3 CHO KB NGAN MACH | Wind - Type 3 cho khảo sát ngắn mạch
- Chi tiết các thông số thể hiện trong từng Sheet

## SOLAR&WIND-TYPE4
CHÚ THÍCH
Enter input | input data |  | dữ liệu đầu vào/ tham khảo số của file, thay đổi tùy từng dự án và tiêu chí
Enter input | key data |  | dữ liệu đầu vào tiên quyết cho mô hình, ảnh hưởng lớn đến kết quả mô phỏng
Fix | tham số mặc định |  | chưa nghiên cứu tính ảnh hưởng đến mô hình, người dùng nghiên cứu thêm
Các thông số đầu vào cần nhập
Hạng mục |  | Giá trị | Chú thích
Tên nhà máy |  | Solar
Công suất nhà máy: |  | 60 | MW
Bus 22kV khảo sát |  | 991087 | Bus sơ cấp của nhà máy
Bus 220/110kV khảo sát |  | 191087 | Bus thứ cấp của nhà máy (đấu nối vào hệ thống)
Kịch bản |  | 1 | 0: Sử dụng mô hình để khảo sát ngắn mạch; 1: Sử dụng mô hình để khảo sát biến động CS theo thời tiết
|  |  | Data dùng để copy vào file *.dyr: | //Solar
|  |  |  | 991087 | 'USRMDL' | 1 | 'PVGU1' | 101 | 1 | 0 | 9 | 3 | 3 | 0.02 | 0.02 | 0.4 | 0.9 | 1.11 | 1.2 | 2 | 2 | 0.02 | /
|  |  |  | 991087 | 'USRMDL' | 1 | 'PVEU1' | 102 | 0 | 4 | 24 | 10 | 4 | 191087 | 0 | 1 | 0 | 0.15 | 18 | 5 | 0.05 | 0.1 | 0 | 0.08 | 0.47 | -0.47 | 1.1 | 0 | 0.5 | -0.5 | 0.05 | 0.1 | 0.9 | 1.1 | 120 | 0.05 | 0.05 | 1.7 | 1.11 | 1.11 | 60 | /
|  |  |  | 991087 | 'USRMDL' | 1 | 'PANELU1' | 103 | 0 | 0 | 5 | 0 | 1 | 0.16 | 0.38 | 0.59 | 0.85 | 1 | /
|  |  |  | 991087 | 'USRMDL' | 1 | 'IRRADU1' | 104 | 0 | 1 | 20 | 0 | 1 | 1 | 5 | 1000 | 8 | 1000 | 13 | 300 | 38 | 300 | 43 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | /
Chi tiết thông số của các mô hình
PV Converter
PVGU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'PVGU1' 101 10 9 3 3 CON(J) to CON(J+8) /
| J | 0.02 | TlqCmd, Converter time constant for IQcmd, second
| J+1 | 0.02 | TlpCmd, Converter time constant for IPcmd, second |  | 991081 'USRMDL' 1 'PVGU1' 101 1 0 9 3 3
| J+2 | 0.4 | VLVPL1, Low voltage power logic (LVPL) voltage 1, pu |  | 0.20000E-01 0.20000E-01 0.40000 0.90000
| J+3 | 0.9 | VLVPL2, LVPL voltage 2, pu |  | 1.1100 1.2000 2.0000 2.0000 0.20000E-01 /
| J+4 | 1.11 | GLVPL gain
| J+5 | 1.2 | VHVRCR, High voltage reactive current (HVRC) logic voltage, pu
| J+6 | 2 | CURHVRCR, max. reactive current at VHVRCR, pu
| J+7 | 2 | Rip_LVPL, Rate of LVACR active current change
| J+8 | 0.02 | T_LVPL, voltage sensor for LVACR time constants
| STATES | Description
| K | Converter lag for Ipcmd
| K+1 | Converter lag for Iqcmd
| K+2 | Voltage sensor for LVACR
| VARs | Description
| L through L+2 | For internal use
Electrical Control Model for PV Converter
PVEU1
| ICONS | Value | Description | Diễn giải | IBUS ' USRMDL' ID 'PVEU1' 102 0 4 24 10 4 ICON(M) to ICON(M+3) CON(J) to CON(J+23) /
| M | 191087 | Remote bus # for voltage control; 0 for local control | Bus thứ cấp của nhà máy (đấu nối vào hệ thống)
| M+1 | 0 | PFAFLG: |  | 991081 'USRMDL' 1 'PVEU1' 102 0 4 24 10 4
|  |  | • 1 if PF fast control enabled |  | 191081 0 1 0
|  |  | • 0 if PF fast control disabled |  | 0.15000 18.000 5.0000 0.50000E-01 0.10000
| M+2 | 1 | VARFLG: |  | 0.0000 0.80000E-01 0.47000 -0.47000 1.1000
|  |  | • 1 if Qord is provided by WindVar |  | 0.0000 0.50000 -0.50000 0.50000E-01 0.10000
|  |  | • 0 if Qord is not provided by WindVar, if VARFLG = PFAFLG = 0 then Qord is provided as as Qref = const |  | 0.90000 1.1000 120.00 0.50000E-01 0.50000E-01
| M+1 | 0 | PQFLG: P/Q priority flag |  | 1.7000 1.1100 1.1100 100.00 /
• 0 - Q priority
• 1 - P priority
| CONs | Value | Description | Diễn giải
| J | 0.15 | Tw, Filter time constant in voltage regulator (sec)
| J+1 | 18 | Kpv, Proportional gain in voltage regulator(pu)
| J+2 | 5 | Kiv, Integrator gain in voltage regulator (pu)
| J+3 | 0.05 | Kpp, Proportional gain in torque regulator (pu)
| J+4 | 0.1 | Kip, Integrator gain in torque regulator (pu
| J+5 | 0 | Kf, rate feedback gain (pu)
| J+6 | 0.08 | Tf, rate feedbacktime constant (sec.)
| J+7 | 0.47 | Qmx, Max limit in voltage regulator (pu)
| J+8 | -0.47 | Qmn, Min limit in voltage regulator (pu)
| J+9 | 1.1 | IPmax, Max active current limit (pu)
| J+10 | 0 | Trv, voltage sensor time constant (sec.)
| J+11 | 0.5 | dPMX, maximum power order rate (pu)
| J+12 | -0.5 | dPMN, minimum power order rate (pu)
| J+13 | 0.05 | Tpower, Power reference filter time constant, sec.
| J+14 | 0.1 | KQi, volt/Mvar gain
| J+15 | 0.9 | Vmincl, min. voltage limit
| J+16 | 1.1 | Vmaxcl, max. voltage limit
| J+17 | 120 | KVi, Int. volt/Term. voltage gain
| J+18 | 0.05 | Tv, Lag in WindVar controller (sec)
| J+19 | 0.05 | Tp, Pelec filter in fast PF controller (sec)
| J+20 | 1.7 | ImaxTD, Converter current limit (pu)
| J+21 | 1.11 | Iphl, Hard active current limit (pu)
| J+22 | 1.11 | Iqhl, Hard reactive current limit (pu)
| J+23 | 60 | PMX, Max power from PV plant, MW | Công suất đặt của nhà máy
| STATES | Description
| K | Filter in Voltage regulator
| K+1 | Integrator in Voltage regulator
| K+2 | Integrator in active power regulator
| K+3 | Active power regulator feedback
| K+4 | Voltage sensor
| K+5 | Power reference filter
| K+6 | Mvar/Vref integrator
| K+7 | Verror/lnternal machine voltage integrator
| K+8 | Lag of the WindVar controller
| K+9 | Input filter of PELEC for fast PF controller
PV I-P Characteristics
PANELU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'PANELU1' 103 0 0 5 0 1 CON(J) to CON(J+4) /
| J | 0.16 | PDCMAX200, maximum power of panel at an irradiance of 200 W/ m2, pu on PDCMAX1000 base | Tỷ lệ Pphát/Pđặt tại mức bức xạ 200 W/ m2
| J+1 | 0.38 | PDCMAX400, maximum power of panel at an irradiance of 400 W/ m2, pu on PDCMAX1000 base | Tỷ lệ Pphát/Pđặt tại mức bức xạ 400 W/ m2 | 991081 'USRMDL' 1 'PANELU1' 103 0 0 5 0 1
| J+2 | 0.59 | PDCMAX600, maximum power of panel at an irradiance of 600 W/ m2, pu on PDCMAX1000 base | Tỷ lệ Pphát/Pđặt tại mức bức xạ 600 W/ m2 | 0.160 0.380 0.590 0.850 1.000 /
| J+3 | 0.85 | PDCMAX800, maximum power of panel at an irradiance of 800 W/ m2, pu on PDCMAX1000 base | Tỷ lệ Pphát/Pđặt tại mức bức xạ 800 W/ m2
| J+4 | 1 | PDCMAX1000, maximum power of panel at an irradiance of 1000 | Tỷ lệ Pphát/Pđặt tại mức bức xạ 1000 W/ m2
| VARs | Description
| L | DC power from PV array
PV Irradiance Profile
IRRADU1
| ICONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'IRRADU1' 104 0 1 20 0 1 ICON(M), CON(J) to CON(J+19) /
| M | 1 | In Service Flag: | Tùy chọn 2 chế độ của model:
|  |  | • 1 : model is in service | 1: Sử dụng model này | 991081 'USRMDL' 1 'IRRADU1' 104 0 1 20 0 1 1
|  |  | • 0: model is OFF | 0: Không sử dụng model này | 5.000 1000.0 15.000 1000.0 18.000 100.0 55.000 100.0 58.000 1000.0
0.000 0.0 0.000 0.0 0.000 0.0 0.000 0.0 0.000 0.0/
| CONs | Value | Description | Diễn giải
| J | 5 | TIME1, Time of first data point, sec | Chi tiết tham khảo hình kế bên | NOTE: Trong trường hợp các khảo sát khác biến động thời tiết thì set M = 0
| J+1 | 1000 | IRRADIANCE1, Irradiance at first data point, W/m2
| J+2 | 8 | TIME2, Time of second data point, sec
| J+3 | 1000 | IRRADIANCE2, Irradiance at second data point, W/m2
| J+4 | 13 | TIME3, Time of third data point, sec
| J+5 | 300 | IRRADIANCE3, Irradiance at third data point, W/m2
| J+6 | 38 | TIME4, Time of fourth data point, sec
| J+7 | 300 | IRRADIANCE4, Irradiance at forth data point, W/m2
| J+8 | 43 | TIME5, Time of fifth data point, sec
| J+9 | 1000 | IRRADIANCE5, Irradiance at fifth data point, W/m2
| J+10 | 0 | TIME6, Time of sixth data point, sec
| J+11 | 0 | IRRADIANCE6, Irradiance at sixth data point, W/m2
| J+12 | 0 | TIME7, Time of seventh data point, sec
| J+13 | 0 | IRRADIANCE7, Irradiance at seventh data point, W/m2
| J+14 | 0 | TIME8, Time of eighth data point, sec
| J+15 | 0 | IRRADIANCE8, Irradiance at eighth at point, W/m2
| J+16 | 0 | TIME9, Time of ninth data point, sec
| J+17 | 0 | IRRADIANCE9, Irradiance at ninth data point, W/m2
| J+18 | 0 | TIME10, Time of tenth data point, sec
| J+19 | 0 | IRRADIANCE10, Irradiance at tenth data point, W/m2
| VARs | Description
| L | DC power from PV array
NOTE: A maximum of 10 pairs of time versus irradiance may be specified. The unused pairs should be entered as zero. TIME1 should be greater than 0 as the initial irradiance calculated from the load flow output

## WIND-TYPE3 CHO KB BDCS
CHÚ THÍCH
Enter input | input data |  | dữ liệu đầu vào/ tham khảo số của file, thay đổi tùy từng dự án và tiêu chí
Enter input | key data |  | dữ liệu đầu vào tiên quyết cho mô hình, ảnh hưởng lớn đến kết quả mô phỏng
Fix | tham số mặc định |  | chưa nghiên cứu tính ảnh hưởng đến mô hình, người dùng nghiên cứu thêm
Các thông số đầu vào cần nhập (Tham khảo mô hình điện gió Type 3 công suất 300MW
Hạng mục |  | Giá trị | Chú thích
Tên nhà máy |  | Khai Long WPP
Công suất nhà máy: |  | 300 | MW
Bus 22kV khảo sát |  | 991061 | Bus sơ cấp của nhà máy
Bus 220/110kV khảo sát |  | 191061 | Bus thứ cấp của nhà máy (đấu nối vào hệ thống)
|  |  | Data dùng để copy vào file *.dyr: | //Khai Long WPP
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWTGCU1' | 101 | 1 | 2 | 18 | 3 | 3 | 200 | 0 | 1.5 | 0.8 | 0.5 | 0.9 | 1.22 | 1.2 | 2 | 0.4 | 0.8 | 10 | 0.02 | 0 | 0 | 0.5 | 0.167 | 0.9 | 0.925 | 0 | /
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWTECU1' | 102 | 0 | 9 | 67 | 18 | 16 | 191061 | 0 | 1 | 0 | 0 | 191061 | 991061 | '1' | 1 | 0.15 | 18 | 5 | 0 | 0 | 0.05 | 3 | 0.85 | 1 | 0.04 | 0.298 | -0.298 | 1.12 | 0.02 | 0.45 | -0.45 | 60 | 0.1 | 0.9 | 1.1 | 40 | 0.5 | 1.45 | 0.05 | 0.05 | 1 | 0.15 | 0.96 | 0.996 | 1.004 | 1.04 | 1 | 0.95 | 0.95 | 0.4 | 1 | 0.2 | 1 | 0.25 | -1 | 15 | 25 | 3 | -0.9 | 8 | 0.2 | 10 | 1 | 1.7 | 1.12 | 1.25 | 5 | 0 | 0 | 0 | 0.0025 | 1 | 5.5 | 0.1 | -1 | 0.1 | 0 | 0.1 | -0.1 | 0.7 | 0.12 | -0.12 | /
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWT2MU1' | 103 | 0 | 1 | 5 | 4 | 3 | 0 | 9 | 0 | 0 | 1.246 | 1.5 | /
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWTPTU1' | 104 | 0 | 2 | 10 | 3 | 3 | 0 | 0 | 0.3 | 150 | 25 | 3 | 30 | -4 | 27 | -10 | 10 | 1 | /
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWTARU1' | 105 | 0 | 1 | 9 | 1 | 4 | 0 | 20 | 0 | 27 | -4 | 0 | 1.225 | 35.25 | 72 | 1200 | /
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWTGDU1' | 106 | 0 | 1 | 6 | 0 | 4 | 0 | 25 | 60 | 12 | 8 | 13 | -12 | /
Chi tiết thông số của các mô hình
GE Wind Turbine Generator/Converter
GEWTGCU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWTGCU1' 101 1 2 18 3 3 ICON(M) to ICON(M+l) CON(J) to CON(J+l7) /
| J | 1.5 | PRATE, rated power of the original unit, in MW | Công suất định mức của 1 turbine
| J+1 | 0.8 | XEq, equivalent reactance for current injection, in pu on MBASE | Trở kháng turbine, lấy theo giá trị theo file .sav | 991061 'USRMDL' 1 'GEWTGCU1' 101 1 2 18 3 3 200 0
| J+2 | 0.5 | VLVPLi, LVPL voltage 1 |  | 1.500 0.80000 0.50000 0.90000 1.2200 1.2000
| J+3 | 0.9 | VLvPL2,LVPL voltage 2 |  | 2.0000 0.40000 0.80000 10.000 0.20000E-01 0.0000
| J+4 | 1.22 | Glvpl, LVPL gain |  | 0.0000 0.50000 0.16700 0.90000 0.92500 0.0000 /
| J+5 | 1.2 | Vhvrcr2, HVRCR voltage 2
| J+6 | 2 | CURHvRcR2, max reactive current at VHVRCR2
| J+7 | 0.4 | VLVACR1, low voltage active current regulation logic, voltage 1 |  | NOTE:
| J+8 | 0.8 | VLVACR2, LVACR logic, voltage 2 |  | - Tùy vào từng dự án thì set Prate và M (Number of original WTs) -> Pgen = Prate*M
| J+9 | 10 | Rip_LVPL, rate of LVACR active current change |  | - Xgen = 0.8 (trong file chạy xác lập)
| J+10 | 0.02 | T_LVPL, voltage sensor for LVACR time constants
| J+11 | 0 | LVPL 1st voltage point
| J+12 | 0 | LVPL 1st power point
| J+13 | 0.5 | LVPL 2nd voltage point
| J+14 | 0.167 | LVPL 2nd power point
| J+15 | 0.9 | LVPL 3rd voltage point
| J+16 | 0.925 | LVPL 3rd power point
| J+17 | 0 | Impedance for changing IQCMD to voltage signal
| ICONs | Value | Description | Diễn giải
| M | 200 | Number of original WTs lumped up to the model equivalent | Số lượng turine = Công suất NM/Công suất định mức của 1 turbine
| M+1 | 0 | Full converter flag
• 0 : DFIG
• 1 :FSC
| STATEs | Description
| K | Converter lag for Ipcmd
| K+1 | Converter lag for Eqcmd or Iqcmd
| K+2 | Voltage sensor for LVPL
| VARs | Description
| L | VMACC,, Vterm magnitude on previous iteration
| L+1 | VAACC, Vterm angle on previous iteration
| L+2 | deltaQ, overvoltage corr. factor
GE Wind Turbine Electrical Control
GEWTECU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWTECU1' 102 0 9 67 18 16 ICON(M) to ICON(M+8) CON(J) to CON(J+66) /
| J | 0.15 | Tfv, filter time constant in voltage regulator (sec)
| J+1 | 18 | Kpv, proportional gain in Voltage regulator(pu) |  | 991061 'USRMDL' 1 'GEWTECU1' 102 0 9 67 18 16
| J+2 | 5 | Kiv, integrator gain in Voltage regulator (pu) |  | 191061 0 1 0 0 191061 991061 '1' 1
| J+3 | 0 | Rc, line drop compensation resistance (pu) |  | 0.15000 18.000 5.0000 0.0000 0.0000
| J+4 | 0 | Xc, line drop compensation reactance (pu) |  | 0.50000E-01 3.0000 0.60000 1.1200 0.40000E-01
| J+5 | 0.05 | Tfp, filter time constant in Torque regulator (sec) |  | 0.29800 -0.29800 1.1200 0.20000E-01 0.45000
| J+6 | 3 | Kpp, proportional gain in Torque regulator(pu) |  | -0.45000 60.000 0.10000 0.90000 1.1000
| J+7 | 0.85 | Kip, integrator gain in Torque regulator (pu) |  | 40.000 0.50000 1.4500 0.50000E-01 0.50000E-01
| J+8 | 1 | Pmax, maximum limit in Torque regulator (pu) |  | 1.0000 0.15000 0.96000 0.99600 1.0040
| J+9 | 0.04 | Pmin, minimum limit in Torque regulator (pu) |  | 1.0400 1.0000 0.95000 0.95000 0.40000
| J+10 | 0.298 | Qmax, maximum limit in Voltage regulator (pu) | Giới hạn trên và dưới của Q, ảnh hưởng đến việc tạo ra file động, và được hiệu chỉnh tùy thuộc từng dự án | 1.0000 0.20000 1.0000 0.25000 -1.0000
| J+11 | -0.298 | Qmin, minimum limit in Voltage regulator (pu) |  | 15.000 25.000 3.0000 -0.90000 8.0000
| J+12 | 1.12 | IPmax, maximum active current limit (pu) |  | 0.20000 10.000 1.0000 1.7000 1.1200
| J+13 | 0.02 | Trv, voltage sensor time constant (sec) |  | 1.2500 5.0000 0.0000 0.0000 0.0000
| J+14 | 0.45 | RPmax, maximum power order derivative (pu) |  | 0.25000E-02 1.0000 5.5000 0.10000 -1.0000
| J+15 | -0.45 | RPmIn, minimum power order derivative (pu) |  | 0.10000 0.0000 0.10000 -0.10000 0.70000
| J+16 | 60 | TPoweR, power reference filter time constant (sec) |  | 0.12000 -0.12000 /
| J+17 | 0.1 | KQU Volt/MVAR gain
| J+18 | 0.9 | VmIncl, minimum voltage limit
| J+19 | 1.1 | Vmaxcl, maximum voltage limit
| J+20 | 40 | KV¦f int. voltage/terminal voltage gain
| J+21 | 0.5 | XImIn, minimum limit
| J+22 | 1.45 | XImax, maximum limit
| J+23 | 0.05 | Tv, lag in WindVar controller
| J+24 | 0.05 | TP, Pelec filter in fast PF controller
| J+25 | 1 | Fn, a portion of on-line wind turbines
| J+26 | 0.15 | TPav, Pavail filter time constant (sec)
| J+27 | 0.96 | FRa, frequency response curve
| J+28 | 0.996 | FRb, frequency response curve
| J+29 | 1.004 | FRc, frequency response curve
| J+30 | 1.04 | FRd, frequency response curve
| J+31 | 1 | PFRa, frequency response curve
| J+32 | 0.95 | PFRb, frequency response curve
| J+33 | 0.95 | PFRc, frequency response curve
| J+34 | 0.4 | PFRd, frequency response curve
| J+35 | 1 | PFRmax, maximum Pavail
| J+36 | 0.2 | PFRmIn, minimum Pavail
| J+37 | 1 | TW, power command rate limit time constant (sec)
| J+38 | 0.25 | Tlvpl, LVPL sensor (sec)
| J+39 | -1 | VLVPL, LVPL breakpoint
| J+40 | 15 | SPDW1, initial arbitrary wind speed (m/sec) | Tốc độ gió khởi tạo của turbine
| J+41 | 25 | SPDWMAX, maximum wind speed (m/sec) | Nếu tốc gió lớn hơn 25m/s thì turbine dừng hoạt động (P=0)
| J+42 | 3 | SPDWMIN, minimum wind speed (m/sec) | Nếu tốc gió nhỏ hơn 3m/s thì turbine không phát công suất (P=0)
| J+43 | -0.9 | SPDLOW, low rotor speed to trip WTG
| J+44 | 8 | WTTHRES, high wind trip threshold
| J+45 | 0.2 | EBST, braking resistor energy threshold
| J+46 | 10 | KDBR, braking resistor controller gain
| J+47 | 1 | PDBRMAX, breaking resistor power error maximum limit
| J+48 | 1.7 | IMAXTD, converter current limit
| J+49 | 1.12 | IPHL, hard active current limit
| J+50 | 1.25 | IQHL, hard reactive current limit
| J+51 | 5 | TLPqD, reactive droop time constant
| J+52 | 0 | KqD, reactive droop gain
| J+53 | 0 | XqD, reactive droop synthesizing impedance
| J+54 | 0 | KWI, wind inertia gain
| J+55 | 0.0025 | DBWI, wind inertia deadband
| J+56 | 1 | TLPWI, wind inertia filter time constant
| J+57 | 5.5 | TWOWI, wind inertia washout time constant
| J+58 | 0.1 | URLWI, wind inertia up rate ramp limit
| J+59 | -1 | DRLWI, wind inertia down rate ramp limit
| J+60 | 0.1 | PMXWI, wind inertia maximum additional power
| J+61 | 0 | PMNWI, wind inertia minimum additional power
| J+62 | 0.1 | VERmx, reactive power control maximum error signal
| J+63 | -0.1 | VERmn, reactive power control minimum error signal
| J+64 | 0.7 | VFRZ, reactive power control freeze voltage
| J+65 | 0.12 | QZPMX, Qmax limit in zero power mode
| J+66 | -0.12 | QZPMN, Qmin limit in zero power mode
| ICONs | Value | Description | Diễn giải
| M | 191061 | Remote bus number for voltage control
| M+1 | 0 | PFAflg
• 1 - if fast PF control enabled
| M+2 | 1 | varflg
• 1 - if Qord is provided by WindVar If VARFLG=PFAFLG=0 then Qordr is provided as a Qref=const
| M+3 | 0 | APCflg, active power control flag
| M+4 | x | FRFLG, frequency flag
| M+5 | 0 | PQflg
• 0 - Q priority
• 1 - P priority
| M+6 | 191061 | Qdroop Branch "From Bus"a
| M+7 | 991061 | Qdroop Branch "To Bus"a
| M+8 | 1' | Qdroop Branch "Id" (enter in single quotes)
| M+9 | 1 | WRflg, wind free enabling flag
| STATEs | Description
| K | Filter in Voltage regulator
| K+1 | Integrator in Voltage regulator
| K+2 | Filter in Torque regulator
| K+3 | Integrator in Torque regulator
| K+4 | Voltage sensor
| K+5 | Power reference filter
| K+6 | Mvar/Volt integrator
| K+7 | Volt/Mvar integrator
| K+8 | Lag of the WindVar controller
| K+9 | Input filter of PELEC for fast PF controller
| K+10 | Input filter for Pavail
| K+11 | Power response rate limit
| K+12 | LVPL limit
| K+13 | High wind speed trip integrator
| K+14 | Braking resistor integrator
| K+15 | Filter in Reactive Droop
| K+16 | Filter in WindInertia
| K+17 | Washout in WindInertia
| VARs | Description
| L | Remote bus reference voltage
| L+1 | Q reference if PFAFLG=0 and VARFLG=0
| L+2 | PF angle reference if PFAFLG = 1
| L+3 | Branch MW for Qdroop
| L+4 | Branch Mvar for Qdroop
| L+5 | Branch MVA for Qdroop
| L+6 | dpwi, WindInertia output
| L+7 | Auxiliary test signal
| L+8 | APC Freq Relay Timer
| L+9 | Available power from the wind, pu on machine base
| L+10 | Active power control output, pu on machine base
| L+11 | Rotor speed for available power
| L+12 | Braking resistor power, pu on machine base
| L+13 | Wind speed for available power
| L+14 | Real current command (WIPCMD), pu on machine base
| L+15 | Reactive current/voltage command (WIQCMD/WEQCMD), pu on machine base
GE Wind Turbine Two Mass Shaft
GEWT2MU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWT2MU1' 103 0 1 5 4 3 0 CON(J) to CON(J+4) /
| J | 9 | H, total inertia of the drive train (MW*sec/MVA) | Hệ số quán tính của hệ thống truyền lực
| J+1 | 0 | DAMP, machine damping factor pu P/pu Speed |  | 991061 'USRMDL' 1 'GEWT2MU1' 103 0 1 5 4 3 0
| J+2 | 0 | HTfrac, turbine inertia fraction (Hturb/H) |  | 9.0000 0.0000 0.0000 1.246 1.500 /
| J+3 | 1.246 | FREQ-¦, first shaft torsional resonant frequency (Hz)
| J+4 | 1.5 | DSHAFT, shaft damping factor |  | NOTE | Đối với mô phỏng biến động công suất do thời tiết, cần đặt hệ số quán tính này cao để turbine có khả năng phát CS ổn định.
Trong trường hợp ở đây chọn H = 9 ứng với công suất nhà máy là 300MW. Đối với từng dự án cụ thể cần điều chỉnh H cho phù hợp
| ICONs | Value | Description
| M |  | For internal use (user to input 0)
| STATEs | Description
| K | Shaft twist angle (radians)
| K+1 | Turbine rotor speed deviation (pu)
| K+2 | Generator speed deviation (pu)
| K+3 | Generator angle deviation (degrees)
| VARs | Description
| L | Paero on the rotor blade side (pu)
| L+1 | Initial rotor slip (pu)
| L+2 | Initial internal angle (degrees)
| L+3 | Cp, Current Cp
GE Wind Turbine Pitch Control
GEWTPTU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWTPTU1' 104 0 2 10 3 3 0 0 CON(J) to CON(J+9) /
| J | 0.3 | TP, time constant of the output lag (sec)
| J+1 | 150 | Kppt, proportional gain of PI regulator (pu) |  | 991061 'USRMDL' 1 'GEWTPTU1' 104 0 2 10 3 3 0 0
| J+2 | 25 | Kipt, tntegrator gain of PI regulator (pu) |  | 0.30000 150.00 25.000 3.0000 30.000
| J+3 | 3 | KPC, proportional gain of the compensator (pu) |  | -4.0000 27.000 -10.000 10.000 1.000 /
| J+4 | 30 | KIC, integrator gain of the compensator (pu)
| J+5 | -4 | 0MIN, lower pitch angle limit (degrees)
| J+6 | 27 | 0MAX, upper pitch angle limit (degrees)
| J+7 | -10 | d0/dtMIN, lower pitch angle rate limit (degrees/sec)
| J+8 | 10 | d0/dtMAX, upper pitch angle rate limit (degrees/sec)
| J+9 | 1 | PREF, power reference
| ICONs | Value | Description
| M |  | For internal use (user to input 0)
| M+1 |  | For internal use (user to input 0)
| STATEs | Description
| K | Output Lag
| K+1 | Pitch Control
| K+2 | Pitch compensator
| VARs | Description
| L | Initial machine rotor speed (pu)
| L+1 | Initial pitch angle (degrees)
| L+2 | Power reference
GE Wind Turbine Aerodynamics
GEWTARU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWTARU1' 105 0 1 9 1 4 0 CON (J) to (J+8) /
| J | 20 | ^MAX, maximum Lambda from Cp curves
| J+1 | 0 | ^MIN, minimum Lambda from Cp curves |  | 991061 'USRMDL' 1 'GEWTARU1' 105 0 1 9 1 4 0
| J+2 | 27 | PITCHMAX, upper limit of pitch angle |  | 20.000 0.0000 27.000 -4.0000 0.000 1.225
| J+3 | -4 | PITCHMIN, lower limit of pitch angle |  | 35.25 72.0000 1200.0 /
| J+4 | 0 | Ta, time constant of the conversion smoothing
| J+S | 1.225 | P, air density (kg/m3)
| J+6 | 35.25 | RADIUS, blade radius (meters)
| J+7 | 72 | GBratio, gear box ratio
| J+8 | 1200 | SYNCHR, synchronous rpm
| ICONs | Value | Description
| M |  | For internal use (user to input 0)
| STATEs | Description
| K | Conversion smoothing lag
| VARs | Description
| L | K_ADJ from initialization
| L+1 | PITCH_INIT, Initial pitch angle
| L+2 | Lambda, current lambda
| L+3 | Cp, Current Cp
GE Wind Turbine Wind Gust and Ramp
GEWTGDU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWTGDUl' 106 0 1 6 0 4 0 CON(J) to CON(J+5) /
| J | 25 | T1G, gust start time (sec) | Chi tiết tham khảo hình kế bên
| J+1 | 60 | Tg, gust duration (sec) |  | 991061 'USRMDL' 1 'GEWTGDU1' 106 0 1 6 0 4 0
| J+2 | 12 | MAXg, Gust peak over Vwb (m/sec) |  | 25.0000 60.0000 12.000 8.0000 13.000 -12.000 /
| J+3 | 8 | T1R, ramp start time (sec)
| J+4 | 13 | T2r, ramp end time (sec) |  | NOTE: Trong trường hợp các khảo sát khác biến động thời tiết thì set T1G = T1R = T2R = 9999 và MAXr = 0
| J+5 | -12 | MAXr, ramp maximum over Vwb (m/sec)
Với các nhập liệu ta ở mô hình GEWTDU1 được đưa ra ta sẽ được đồ thị như sau :
| ICONs | Value | Description
| M |  | For internal use (user to input 0)
| VARs | Description
| L | VW, Effective wind speed
| L+1 | VWG, gust component (m/sec)
| L+2 | VWR, ramp component (m/sec)
| L+3 | VWB, initial wind speed
Tg
Công suất turbine tương ứng cho nhà máy công suất 300MW
MAXg
T1G
MAX
T1R
T2R
RAMP
GUST
SPDW1
Note on D189: Đối với mô phỏng biến động công suất do thời tiết, cần đặt hệ số quan tính này cao. Trong trường hợp ở đây chọn H =9 ứng với công suất nhà máy là 300MW. Đối với từng dự án cụ thể cần điều chỉnh H cho phù hợp

## WIND-TYPE3 CHO KB NGAN MACH
CHÚ THÍCH
Enter input | input data |  | dữ liệu đầu vào/ tham khảo số của file, thay đổi tùy từng dự án và tiêu chí
Enter input | key data |  | dữ liệu đầu vào tiên quyết cho mô hình, ảnh hưởng lớn đến kết quả mô phỏng
Fix | tham số mặc định |  | chưa nghiên cứu tính ảnh hưởng đến mô hình, người dùng nghiên cứu thêm
Các thông số đầu vào cần nhập (Tham khảo mô hình điện gió Type 3 công suất 300MW
Hạng mục |  | Giá trị | Chú thích
Tên nhà máy |  | Khai Long WPP
Công suất nhà máy: |  | 300 | MW
Bus 22kV khảo sát |  | 991061 | Bus sơ cấp của nhà máy
Bus 220/110kV khảo sát |  | 191061 | Bus thứ cấp của nhà máy (đấu nối vào hệ thống)
|  |  | Data dùng để copy vào file *.dyr: | //Khai Long WPP
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWTGCU1' | 101 | 1 | 2 | 18 | 3 | 3 | 200 | 0 | 1.5 | 0.8 | 0.5 | 0.9 | 1.22 | 1.2 | 2 | 0.4 | 0.8 | 10 | 0.02 | 0 | 0 | 0.5 | 0.167 | 0.9 | 0.925 | 0 | /
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWTECU1' | 102 | 0 | 9 | 67 | 18 | 16 | 191061 | 0 | 1 | 0 | 0 | 191061 | 991061 | '1' | 1 | 0.15 | 18 | 5 | 0 | 0 | 0.05 | 3 | 0.85 | 1 | 0.04 | 0.298 | -0.298 | 1.12 | 0.02 | 0.45 | -0.45 | 60 | 0.1 | 0.9 | 1.1 | 40 | 0.5 | 1.45 | 0.05 | 0.05 | 1 | 0.15 | 0.96 | 0.996 | 1.004 | 1.04 | 1 | 0.95 | 0.95 | 0.4 | 1 | 0.2 | 1 | 0.25 | -1 | 15 | 25 | 3 | -0.9 | 8 | 0.2 | 10 | 1 | 1.7 | 1.12 | 1.25 | 5 | 0 | 0 | 0 | 0.0025 | 1 | 5.5 | 0.1 | -1 | 0.1 | 0 | 0.1 | -0.1 | 0.7 | 0.12 | -0.12 | /
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWT2MU1' | 103 | 0 | 1 | 5 | 4 | 3 | 0 | 9 | 0 | 0 | 1.246 | 1.5 | /
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWTPTU1' | 104 | 0 | 2 | 10 | 3 | 3 | 0 | 0 | 0.3 | 150 | 25 | 3 | 30 | -4 | 27 | -10 | 10 | 1 | /
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWTARU1' | 105 | 0 | 1 | 9 | 1 | 4 | 0 | 20 | 0 | 27 | -4 | 0 | 1.225 | 35.25 | 72 | 1200 | /
|  |  |  | 991061 | 'USRMDL' | 1 | 'GEWTGDU1' | 106 | 0 | 1 | 6 | 0 | 4 | 0 | 9999 | 35 | -12 | 9999 | 9999 | 0 | /
Chi tiết thông số của các mô hình
GE Wind Turbine Generator/Converter
GEWTGCU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWTGCU1' 101 1 2 18 3 3 ICON(M) to ICON(M+l) CON(J) to CON(J+l7) /
| J | 1.5 | PRATE, rated power of the original unit, in MW
| J+1 | 0.8 | XEq, equivalent reactance for current injection, in pu on MBASE |  | 991061 'USRMDL' 1 'GEWTGCU1' 101 1 2 18 3 3 200 0
| J+2 | 0.5 | VLVPLi, LVPL voltage 1 |  | 1.500 0.80000 0.50000 0.90000 1.2200 1.2000
| J+3 | 0.9 | VLvPL2,LVPL voltage 2 |  | 2.0000 0.40000 0.80000 10.000 0.20000E-01 0.0000
| J+4 | 1.22 | Glvpl, LVPL gain |  | 0.0000 0.50000 0.16700 0.90000 0.92500 0.0000 /
| J+5 | 1.2 | Vhvrcr2, HVRCR voltage 2
| J+6 | 2 | CURHvRcR2, max reactive current at VHVRCR2
| J+7 | 0.4 | VLVACR1, low voltage active current regulation logic, voltage 1 |  | NOTE:
| J+8 | 0.8 | VLVACR2, LVACR logic, voltage 2 |  | - Tùy vào từng dự án thì set Prate và M (Number of original WTs) -> Pgen = Prate*M
| J+9 | 10 | Rip_LVPL, rate of LVACR active current change |  | - Xgen = 0.8 (trong file chạy xác lập)
| J+10 | 0.02 | T_LVPL, voltage sensor for LVACR time constants
| J+11 | 0 | LVPL 1st voltage point
| J+12 | 0 | LVPL 1st power point
| J+13 | 0.5 | LVPL 2nd voltage point
| J+14 | 0.167 | LVPL 2nd power point
| J+15 | 0.9 | LVPL 3rd voltage point
| J+16 | 0.925 | LVPL 3rd power point
| J+17 | 0 | Impedance for changing IQCMD to voltage signal
| ICONs | Value | Description | Diễn giải
| M | 200 | Number of original WTs lumped up to the model equivalent
| M+1 | 0 | Full converter flag
• 0 : DFIG
• 1 :FSC
| STATEs | Description
| K | Converter lag for Ipcmd
| K+1 | Converter lag for Eqcmd or Iqcmd
| K+2 | Voltage sensor for LVPL
| VARs | Description
| L | VMACC,, Vterm magnitude on previous iteration
| L+1 | VAACC, Vterm angle on previous iteration
| L+2 | deltaQ, overvoltage corr. factor
GE Wind Turbine Electrical Control
GEWTECU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWTECU1' 102 0 9 67 18 16 ICON(M) to ICON(M+8) CON(J) to CON(J+66) /
| J | 0.15 | Tfv, filter time constant in voltage regulator (sec)
| J+1 | 18 | Kpv, proportional gain in Voltage regulator(pu) |  | 991061 'USRMDL' 1 'GEWTECU1' 102 0 9 67 18 16
| J+2 | 5 | Kiv, integrator gain in Voltage regulator (pu) |  | 191061 0 1 0 0 191061 991061 '1' 1
| J+3 | 0 | Rc, line drop compensation resistance (pu) |  | 0.15000 18.000 5.0000 0.0000 0.0000
| J+4 | 0 | Xc, line drop compensation reactance (pu) |  | 0.50000E-01 3.0000 0.60000 1.1200 0.40000E-01
| J+5 | 0.05 | Tfp, filter time constant in Torque regulator (sec) |  | 0.29800 -0.29800 1.1200 0.20000E-01 0.45000
| J+6 | 3 | Kpp, proportional gain in Torque regulator(pu) |  | -0.45000 60.000 0.10000 0.90000 1.1000
| J+7 | 0.85 | Kip, integrator gain in Torque regulator (pu) |  | 40.000 0.50000 1.4500 0.50000E-01 0.50000E-01
| J+8 | 1 | Pmax, maximum limit in Torque regulator (pu) |  | 1.0000 0.15000 0.96000 0.99600 1.0040
| J+9 | 0.04 | Pmin, minimum limit in Torque regulator (pu) |  | 1.0400 1.0000 0.95000 0.95000 0.40000
| J+10 | 0.298 | Qmax, maximum limit in Voltage regulator (pu) |  | 1.0000 0.20000 1.0000 0.25000 -1.0000
| J+11 | -0.298 | Qmin, minimum limit in Voltage regulator (pu) |  | 15.000 25.000 3.0000 -0.90000 8.0000
| J+12 | 1.12 | IPmax, maximum active current limit (pu) |  | 0.20000 10.000 1.0000 1.7000 1.1200
| J+13 | 0.02 | Trv, voltage sensor time constant (sec) |  | 1.2500 5.0000 0.0000 0.0000 0.0000
| J+14 | 0.45 | RPmax, maximum power order derivative (pu) |  | 0.25000E-02 1.0000 5.5000 0.10000 -1.0000
| J+15 | -0.45 | RPmIn, minimum power order derivative (pu) |  | 0.10000 0.0000 0.10000 -0.10000 0.70000
| J+16 | 60 | TPoweR, power reference filter time constant (sec) |  | 0.12000 -0.12000 /
| J+17 | 0.1 | KQU Volt/MVAR gain
| J+18 | 0.9 | VmIncl, minimum voltage limit
| J+19 | 1.1 | Vmaxcl, maximum voltage limit
| J+20 | 40 | KV¦f int. voltage/terminal voltage gain
| J+21 | 0.5 | XImIn, minimum limit
| J+22 | 1.45 | XImax, maximum limit
| J+23 | 0.05 | Tv, lag in WindVar controller
| J+24 | 0.05 | TP, Pelec filter in fast PF controller
| J+25 | 1 | Fn, a portion of on-line wind turbines
| J+26 | 0.15 | TPav, Pavail filter time constant (sec)
| J+27 | 0.96 | FRa, frequency response curve
| J+28 | 0.996 | FRb, frequency response curve
| J+29 | 1.004 | FRc, frequency response curve
| J+30 | 1.04 | FRd, frequency response curve
| J+31 | 1 | PFRa, frequency response curve
| J+32 | 0.95 | PFRb, frequency response curve
| J+33 | 0.95 | PFRc, frequency response curve
| J+34 | 0.4 | PFRd, frequency response curve
| J+35 | 1 | PFRmax, maximum Pavail
| J+36 | 0.2 | PFRmIn, minimum Pavail
| J+37 | 1 | TW, power command rate limit time constant (sec)
| J+38 | 0.25 | Tlvpl, LVPL sensor (sec)
| J+39 | -1 | VLVPL, LVPL breakpoint
| J+40 | 15 | SPDW1, initial arbitrary wind speed (m/sec)
| J+41 | 25 | SPDWMAX, maximum wind speed (m/sec)
| J+42 | 3 | SPDWMIN, minimum wind speed (m/sec)
| J+43 | -0.9 | SPDLOW, low rotor speed to trip WTG
| J+44 | 8 | WTTHRES, high wind trip threshold
| J+45 | 0.2 | EBST, braking resistor energy threshold
| J+46 | 10 | KDBR, braking resistor controller gain
| J+47 | 1 | PDBRMAX, breaking resistor power error maximum limit
| J+48 | 1.7 | IMAXTD, converter current limit
| J+49 | 1.12 | IPHL, hard active current limit
| J+50 | 1.25 | IQHL, hard reactive current limit
| J+51 | 5 | TLPqD, reactive droop time constant
| J+52 | 0 | KqD, reactive droop gain
| J+53 | 0 | XqD, reactive droop synthesizing impedance
| J+54 | 0 | KWI, wind inertia gain
| J+55 | 0.0025 | DBWI, wind inertia deadband
| J+56 | 1 | TLPWI, wind inertia filter time constant
| J+57 | 5.5 | TWOWI, wind inertia washout time constant
| J+58 | 0.1 | URLWI, wind inertia up rate ramp limit
| J+59 | -1 | DRLWI, wind inertia down rate ramp limit
| J+60 | 0.1 | PMXWI, wind inertia maximum additional power
| J+61 | 0 | PMNWI, wind inertia minimum additional power
| J+62 | 0.1 | VERmx, reactive power control maximum error signal
| J+63 | -0.1 | VERmn, reactive power control minimum error signal
| J+64 | 0.7 | VFRZ, reactive power control freeze voltage
| J+65 | 0.12 | QZPMX, Qmax limit in zero power mode
| J+66 | -0.12 | QZPMN, Qmin limit in zero power mode
| ICONs | Value | Description | Diễn giải
| M | 191061 | Remote bus number for voltage control
| M+1 | 0 | PFAflg
• 1 - if fast PF control enabled
| M+2 | 1 | varflg
• 1 - if Qord is provided by WindVar If VARFLG=PFAFLG=0 then Qordr is provided as a Qref=const
| M+3 | 0 | APCflg, active power control flag
| M+4 | x | FRFLG, frequency flag
| M+5 | 0 | PQflg
• 0 - Q priority
• 1 - P priority
| M+6 | 191061 | Qdroop Branch "From Bus"a
| M+7 | 991061 | Qdroop Branch "To Bus"a
| M+8 | 1' | Qdroop Branch "Id" (enter in single quotes)
| M+9 | 1 | WRflg, wind free enabling flag
| STATEs | Description
| K | Filter in Voltage regulator
| K+1 | Integrator in Voltage regulator
| K+2 | Filter in Torque regulator
| K+3 | Integrator in Torque regulator
| K+4 | Voltage sensor
| K+5 | Power reference filter
| K+6 | Mvar/Volt integrator
| K+7 | Volt/Mvar integrator
| K+8 | Lag of the WindVar controller
| K+9 | Input filter of PELEC for fast PF controller
| K+10 | Input filter for Pavail
| K+11 | Power response rate limit
| K+12 | LVPL limit
| K+13 | High wind speed trip integrator
| K+14 | Braking resistor integrator
| K+15 | Filter in Reactive Droop
| K+16 | Filter in WindInertia
| K+17 | Washout in WindInertia
| VARs | Description
| L | Remote bus reference voltage
| L+1 | Q reference if PFAFLG=0 and VARFLG=0
| L+2 | PF angle reference if PFAFLG = 1
| L+3 | Branch MW for Qdroop
| L+4 | Branch Mvar for Qdroop
| L+5 | Branch MVA for Qdroop
| L+6 | dpwi, WindInertia output
| L+7 | Auxiliary test signal
| L+8 | APC Freq Relay Timer
| L+9 | Available power from the wind, pu on machine base
| L+10 | Active power control output, pu on machine base
| L+11 | Rotor speed for available power
| L+12 | Braking resistor power, pu on machine base
| L+13 | Wind speed for available power
| L+14 | Real current command (WIPCMD), pu on machine base
| L+15 | Reactive current/voltage command (WIQCMD/WEQCMD), pu on machine base
GE Wind Turbine Two Mass Shaft
GEWT2MU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWT2MU1' 103 0 1 5 4 3 0 CON(J) to CON(J+4) /
| J | 9 | H, total inertia of the drive train (MW*sec/MVA)
| J+1 | 0 | DAMP, machine damping factor pu P/pu Speed |  | 991061 'USRMDL' 1 'GEWT2MU1' 103 0 1 5 4 3 0
| J+2 | 0 | HTfrac, turbine inertia fraction (Hturb/H) |  | 9.0000 0.0000 0.0000 1.246 1.500 /
| J+3 | 1.246 | FREQ-¦, first shaft torsional resonant frequency (Hz)
| J+4 | 1.5 | DSHAFT, shaft damping factor
| ICONs | Value | Description
| M |  | For internal use (user to input 0)
| STATEs | Description
| K | Shaft twist angle (radians)
| K+1 | Turbine rotor speed deviation (pu)
| K+2 | Generator speed deviation (pu)
| K+3 | Generator angle deviation (degrees)
| VARs | Description
| L | Paero on the rotor blade side (pu)
| L+1 | Initial rotor slip (pu)
| L+2 | Initial internal angle (degrees)
| L+3 | Cp, Current Cp
GE Wind Turbine Pitch Control
GEWTPTU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWTPTU1' 104 0 2 10 3 3 0 0 CON(J) to CON(J+9) /
| J | 0.3 | TP, time constant of the output lag (sec)
| J+1 | 150 | Kppt, proportional gain of PI regulator (pu) |  | 991061 'USRMDL' 1 'GEWTPTU1' 104 0 2 10 3 3 0 0
| J+2 | 25 | Kipt, tntegrator gain of PI regulator (pu) |  | 0.30000 150.00 25.000 3.0000 30.000
| J+3 | 3 | KPC, proportional gain of the compensator (pu) |  | -4.0000 27.000 -10.000 10.000 1.000 /
| J+4 | 30 | KIC, integrator gain of the compensator (pu)
| J+5 | -4 | 0MIN, lower pitch angle limit (degrees)
| J+6 | 27 | 0MAX, upper pitch angle limit (degrees)
| J+7 | -10 | d0/dtMIN, lower pitch angle rate limit (degrees/sec)
| J+8 | 10 | d0/dtMAX, upper pitch angle rate limit (degrees/sec)
| J+9 | 1 | PREF, power reference
| ICONs | Value | Description
| M |  | For internal use (user to input 0)
| M+1 |  | For internal use (user to input 0)
| STATEs | Description
| K | Output Lag
| K+1 | Pitch Control
| K+2 | Pitch compensator
| VARs | Description
| L | Initial machine rotor speed (pu)
| L+1 | Initial pitch angle (degrees)
| L+2 | Power reference
GE Wind Turbine Aerodynamics
GEWTARU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWTARU1' 105 0 1 9 1 4 0 CON (J) to (J+8) /
| J | 20 | ^MAX, maximum Lambda from Cp curves
| J+1 | 0 | ^MIN, minimum Lambda from Cp curves |  | 991061 'USRMDL' 1 'GEWTARU1' 105 0 1 9 1 4 0
| J+2 | 27 | PITCHMAX, upper limit of pitch angle |  | 20.000 0.0000 27.000 -4.0000 0.000 1.225
| J+3 | -4 | PITCHMIN, lower limit of pitch angle |  | 35.25 72.0000 1200.0 /
| J+4 | 0 | Ta, time constant of the conversion smoothing
| J+S | 1.225 | P, air density (kg/m3)
| J+6 | 35.25 | RADIUS, blade radius (meters)
| J+7 | 72 | GBratio, gear box ratio
| J+8 | 1200 | SYNCHR, synchronous rpm
| ICONs | Value | Description
| M |  | For internal use (user to input 0)
| STATEs | Description
| K | Conversion smoothing lag
| VARs | Description
| L | K_ADJ from initialization
| L+1 | PITCH_INIT, Initial pitch angle
| L+2 | Lambda, current lambda
| L+3 | Cp, Current Cp
GE Wind Turbine Wind Gust and Ramp
GEWTGDU1
| CONs | Value | Description | Diễn giải | IBUS 'USRMDL' ID 'GEWTGDUl' 106 0 1 6 0 4 0 CON(J) to CON(J+5) /
| J | 9999 | T1G, gust start time (sec)
| J+1 | 35 | Tg, gust duration (sec) |  | 991061 'USRMDL' 1 'GEWTGDU1' 106 0 1 6 0 4 0
| J+2 | -12 | MAXg, Gust peak over Vwb (m/sec) |  | 25.0000 60.0000 12.000 8.0000 13.000 -12.000 /
| J+3 | 9999 | T1R, ramp start time (sec)
| J+4 | 9999 | T2r, ramp end time (sec) |  | NOTE: Trong trường hợp các khảo sát khác biến động thời tiết thì set T1G = T1R = T2R = 9999 và MAXr = 0
| J+5 | 0 | MAXr, ramp maximum over Vwb (m/sec)
Với các nhập liệu ta ở mô hình GEWTDU1 được đưa ra ta sẽ được đồ thị như sau :
| ICONs | Value | Description
| M |  | For internal use (user to input 0)
| VARs | Description
| L | VW, Effective wind speed
| L+1 | VWG, gust component (m/sec)
| L+2 | VWR, ramp component (m/sec)
| L+3 | VWB, initial wind speed
Tg
Công suất turbine tương ứng cho nhà máy công suất 300MW
MAXg
T1G
MAX
T1R
T2R
RAMP
GUST
SPDW1
Note on D189: Đối với mô phỏng biến động công suất do thời tiết, cần đặt hệ số quan tính này cao. Trong trường hợp ở đây chọn H =9 ứng với công suất nhà máy là 300MW. Đối với từng dự án cụ thể cần điều chỉnh H cho phù hợp