## Sheet1
Col_A | Col_B |  | Graphics functions cannot be used when the GUI is not used.
3 | psspy.ascc(1,0,[1,0,0,0,1,2,0,1,0,0],"","") | # File:"Z:\Tinh toan dau noi\Vung Ang 2\PSSE\2018\Lua chon phuong an toi uu (so sanh 4 pa)\PA toi uu2018(co tu-khang o VA; ko tu-khang o Hue)\nganmach2018-2023.py", generated on MON, MAY 12 2008 17:04 | . PSS(R)E SHORT CIRCUIT OUTPUT WED, JUN 16 2021 13:31 . HOME BUS IS : .
|  | psspy.report_output(5,"",[0,0]) | . NAM 2030-PHU TAI CUC DAI-PA1 . 16010 [LAOCAI5 500.00] .
|  | psspy.bsys(1,0,[0.0,0.0],0,[],7,[177041,16010,17010,17012,19030],0,[],0,[]) | . . .
|  | psspy.ascc(1,0,[1,0,0,0,1,2,0,1,0,0],"","") | . *** FAULTED BUS IS : 16010 [LAOCAI5 500.00] *** . 0 LEVELS AWAY .
AT BUS 16010 [LAOCAI5 500.00] AREA 16 (KV L-G) V+: / 0.000/ 0.00 (KV L-G) VA: / 0.000/ 0.00 V0: /221.346/ 174.76
V+: /255.742/ -3.51 V-: / 35.133/ -172.59
THEV. R, X, X/R: POSITIVE 0.00148 0.00952 6.445 NEGATIVE 0.00148 0.00952 6.445 ZERO 0.02221 0.05648 2.543
T H R E E P H A S E F A U L T O N E P H A S E F A U L T
X--------- FROM ----------X AREA CKT I/Z /I+/ AN(I+) /Z+/ AN(Z+) APP X/R /3I0/ AN(3I0) /Z0/ AN(Z0) APP X/R
20010 [VINHYEN5 500.00] 15 1 AMP/OHM 3620.2 -87.77 56.88 84.68 10.741 2188.2 -73.77 33.09 -101.94 4.730
20010 [VINHYEN5 500.00] 15 2 AMP/OHM 3620.2 -87.77 56.88 84.68 10.741 2188.2 -73.77 33.09 -101.94 4.730
3WNDTR [LAOCAI500 ] WND 1 1 AMP/ 2433.6 -76.85 0.0 0.00
3WNDTR [LAOCAI500 ] WND 1 2 AMP/ 2433.6 -76.85 0.0 0.00
TOTAL FAULT CURRENT (AMPS) 12054.8 -83.38 4376.4 -73.77
. PSS(R)E SHORT CIRCUIT OUTPUT WED, JUN 16 2021 13:31 . HOME BUS IS : .
. NAM 2030-PHU TAI CUC DAI-PA1 . 17010 [LAICHAU5 500.00] .
. . .
. *** FAULTED BUS IS : 17010 [LAICHAU5 500.00] *** . 0 LEVELS AWAY .
AT BUS 17010 [LAICHAU5 500.00] AREA 17 (KV L-G) V+: / 0.000/ 0.00 (KV L-G) VA: / 0.000/ 0.00 V0: / 99.226/ -152.36
V+: /199.042/ 28.90 V-: / 99.863/ -149.85
THEV. R, X, X/R: POSITIVE 0.00043 0.00711 16.474 NEGATIVE 0.00043 0.00711 16.474 ZERO 0.00074 0.00704 9.545
T H R E E P H A S E F A U L T O N E P H A S E F A U L T
X--------- FROM ----------X AREA CKT I/Z /I+/ AN(I+) /Z+/ AN(Z+) APP X/R /3I0/ AN(3I0) /Z0/ AN(Z0) APP X/R
17012 [TDLAICHAU5 500.00] 15 1 AMP/OHM 9024.7 -53.74 1.38 85.84 13.750 9988.7 -55.22 23.18 -93.95 14.484
19010 [SONLA15 500.00] 15 1 AMP/OHM 5317.2 -72.03 37.63 85.76 13.494 1433.1 -45.35 21.38 -94.90 11.659
3WNDTR [LAICHAU5_AT1] WND 1 1 AMP/ 1380.5 -40.03 3459.0 -61.49
3WNDTR [LAICHAU5_AT2] WND 1 2 AMP/ 1380.4 -40.04 1994.1 -61.16
TO SHUNT (AMPS) 0.0 0.00 0.0 0.00
TOTAL FAULT CURRENT (AMPS) 16786.4 -57.21 16825.7 -56.38
. PSS(R)E SHORT CIRCUIT OUTPUT WED, JUN 16 2021 13:31 . HOME BUS IS : .
. NAM 2030-PHU TAI CUC DAI-PA1 . 17012 [TDLAICHAU5 500.00] .
. . .
. *** FAULTED BUS IS : 17012 [TDLAICHAU5 500.00] *** . 0 LEVELS AWAY .
AT BUS 17012 [TDLAICHAU5 500.00] AREA 15 (KV L-G) V+: / 0.000/ 0.00 (KV L-G) VA: / 0.000/ 0.00 V0: / 92.468/ -151.36
V+: /195.833/ 29.30 V-: /103.377/ -150.11
THEV. R, X, X/R: POSITIVE 0.00042 0.00707 16.863 NEGATIVE 0.00042 0.00707 16.863 ZERO 0.00051 0.00631 12.310
T H R E E P H A S E F A U L T O N E P H A S E F A U L T
X--------- FROM ----------X AREA CKT I/Z /I+/ AN(I+) /Z+/ AN(Z+) APP X/R /3I0/ AN(3I0) /Z0/ AN(Z0) APP X/R
17010 [LAICHAU5 500.00] 17 1 AMP/OHM 7435.1 -61.28 1.38 85.84 13.750 5504.8 -55.29 43.77 -94.23 13.522
19010 [SONLA15 500.00] 15 1 AMP/OHM 3893.1 -70.66 51.98 84.26 9.947 1700.4 -44.85 18.40 -95.55 10.290
917071 [LAICHAU_H1 15.800] 16 1 AMP/OHM 1469.9 -42.80 0.08 89.82 317.000 2589.7 -59.42 0.00 0.00 0.000
917072 [LAICHAU_H2 15.800] 16 1 AMP/OHM 1469.9 -42.80 0.08 89.82 317.000 2589.7 -59.42 0.00 0.00 0.000
917073 [LAICHAU_H3 15.800] 16 1 AMP/OHM 1469.9 -42.80 0.08 89.82 317.000 2589.7 -59.42 0.00 0.00 0.000
917074 [LAICHAU_H4 15.800] 16 1 AMP/OHM 1469.9 -42.80 0.08 89.82 317.000 2589.7 -59.42 0.00 0.00 0.000
TO SHUNT (AMPS) 0.0 0.00 0.0 0.00
TOTAL FAULT CURRENT (AMPS) 16897.4 -57.11 17514.3 -56.72
. PSS(R)E SHORT CIRCUIT OUTPUT WED, JUN 16 2021 13:31 . HOME BUS IS : .
. NAM 2030-PHU TAI CUC DAI-PA1 . 19030 [PSPPBAC5 500.00] .
. . .
. *** FAULTED BUS IS : 19030 [PSPPBAC5 500.00] *** . 0 LEVELS AWAY .
AT BUS 19030 [PSPPBAC5 500.00] AREA 15 (KV L-G) V+: / 0.000/ 0.00 (KV L-G) VA: / 0.000/ 0.00 V0: /128.739/ -170.03
V+: /210.588/ 11.38 V-: / 81.949/ -166.41
THEV. R, X, X/R: POSITIVE 0.00058 0.00526 9.113 NEGATIVE 0.00058 0.00526 9.113 ZERO 0.00143 0.00819 5.736
T H R E E P H A S E F A U L T O N E P H A S E F A U L T
X--------- FROM ----------X AREA CKT I/Z /I+/ AN(I+) /Z+/ AN(Z+) APP X/R /3I0/ AN(3I0) /Z0/ AN(Z0) APP X/R
19010 [SONLA15 500.00] 15 1 AMP/OHM 5355.5 -60.21 31.38 84.34 10.090 3481.3 -64.51 22.64 -96.25 9.133
19010 [SONLA15 500.00] 15 2 AMP/OHM 5355.5 -60.21 31.38 84.34 10.090 3481.3 -64.51 22.64 -96.25 9.133
21010 [VIETTRI5 500.00] 15 1 AMP/OHM 4096.5 -93.64 31.38 84.34 10.090 3077.9 -65.69 37.37 -95.92 9.649
21012 [PY_VY 500.00] 15 1 AMP/OHM 3210.0 -92.40 31.38 84.34 10.090 1905.5 -62.79 113.97 -106.73 3.326
919051 [TDTNBAC1_H1 15.800] 16 1 AMP/OHM 1623.8 -65.67 0.08 89.46 105.666 2265.2 -80.03 0.00 0.00 0.000
919052 [TDTNBAC1_H2 15.800] 16 1 AMP/OHM 1623.8 -65.67 0.08 89.46 105.666 2265.2 -80.03 0.00 0.00 0.000
919061 [TDTNBAC2_H1 15.800] 16 1 AMP/OHM 1588.4 -65.39 0.08 89.46 105.667 2265.2 -80.03 0.00 0.00 0.000
TOTAL FAULT CURRENT (AMPS) 22107.4 -71.74 18581.9 -70.15
. PSS(R)E SHORT CIRCUIT OUTPUT WED, JUN 16 2021 13:31 . HOME BUS IS : .
. NAM 2030-PHU TAI CUC DAI-PA1 . 177041 [BINHHOA1 110.00] .
. . .
. *** FAULTED BUS IS : 177041 [BINHHOA1 110.00] *** . 0 LEVELS AWAY .
AT BUS 177041 [BINHHOA1 110.00] AREA 31 (KV L-G) V+: / 0.000/ 0.00 (KV L-G) VA: / 0.000/ 0.00 V0: / 37.955/ 179.09
V+: / 49.084/ 0.31 V-: / 11.167/ -175.56
THEV. R, X, X/R: POSITIVE 0.00231 0.00944 4.092 NEGATIVE 0.00231 0.00944 4.092 ZERO 0.01079 0.03121 2.892
T H R E E P H A S E F A U L T O N E P H A S E F A U L T
X--------- FROM ----------X AREA CKT I/Z /I+/ AN(I+) /Z+/ AN(Z+) APP X/R /3I0/ AN(3I0) /Z0/ AN(Z0) APP X/R
177119 [HOAXA1 110.00] 31 1 AMP/OHM 24157.3 -75.58 1.40 78.13 4.756 13024.2 -70.99 0.91 -110.55 2.668
177325 [HBPHUOC21 110.00] 31 1 AMP/OHM 27070.0 -74.85 1.08 78.16 4.770 15471.9 -72.54 1.33 -101.66 4.845
TO SHUNT (AMPS) 0.0 0.00 0.0 0.00
TOTAL FAULT CURRENT (AMPS) 51226.3 -75.20 28493.5 -71.83
Output completed